## AHU
Main Page Title | Meter | Auto/Manual Status | Action | STATUS | COMMAND | Command vs Status Check | RAT | RAT Value Status | Temperature Setpoint | CHW VALVE MODULATION | Delta | Recommended Valve Opening | Valve Opening Status Comment | COMMENT
AHU SUMMARY | AHU 1 BS | AUTO | CHECK | OFF | OFF | OK | 23.1 | OK | 24 | 0 | -0.9 | 0 | OK | NONE
| AHU 2 BS | AUTO | CHECK | OFF | OFF | OK | 28.9 | OK | 24 | 0 | 4.9 | 100 | FAULT | Valve is not open as per the requirement
| AHU 3 BS | AUTO | CHECK | ON | ON | OK | 25.8 | OK | 24 | 45.2 | 1.8 | 100 | FAULT | Valve is not open as per the requirement
| AHU 4 BS | AUTO | CHECK | ON | ON | OK | 23.7 | OK | 18 | 100 | 5.7 | 100 | OK | NONE
| AHU 5 BS | AUTO | CHECK | ON | ON | OK | 22.5 | OK | 18 | 100 | 4.5 | 100 | OK | NONE
| AHU 6 BS | AUTO | CHECK | ON | ON | OK | 20.9 | OK | 18 | 73.3 | 2.9 | 100 | FAULT | Valve is not open as per the requirement
| AHU 7 BS | AUTO | CHECK | ON | ON | OK | 20.5 | OK | 16 | 100 | 4.5 | 100 | OK | NONE
| AHU 8 BS | AUTO | CHECK | ON | ON | OK | 25.8 | OK | 20 | 100 | 5.8 | 100 | OK | NONE
| AHU 9 BS | AUTO | CHECK | ON | ON | OK | 25.4 | OK | 24 | 34 | 1.4 | 100 | FAULT | Valve is not open as per the requirement
| Test1 | MANUAL | XX | OFF | ON | XX | 30 | OK | 18 | 10 | 12 | 100 | OK | NONE
| Test2 | MANUAL | XX | ON | OFF | XX | 35 | FAULT | 20 | 58 | 15 | 100 | OK | NONE
| Test3 | AUTO | CHECK | OFF | ON | FAULT | 16 | FAULT | 22 | 80 | -6 | 0 | FAULT | Valve is open more than requirement

## CHILLERS
Main Page Title | Meter | Chiller Status | Condenser Valve Status | Evaporator Valve Status | Condensor VALVE COMMENT | Evaporator VALVE COMMENT | Evaporator Inlet | Evaporator Outlet | Delta | Evaporator Inlet Status | Evaporator Outlet Status | Evaporator Delta Status
Chiller Summary | Chiller-1 | OFF | OFF | OFF | OK | OK | 11.5 | 8 | 3.5 | FAULT | OK | FAULT
| Chiller-2 | OFF | OFF | OFF | OK | OK | 12.3 | 7.7 | 4.6 | OK | OK | OK
| Chiller-3 | OFF | OFF | OFF | OK | OK | 11.7 | 13.8 | -2.1 | FAULT | FAULT | FAULT
| Test Chiller-1 | ON | OFF | ON | FAULT | OK | 15 | 7 | 8 | FAULT | OK | FAULT
| Test Chiller-2 | ON | ON | OFF | OK | FAULT | 12 | 5 | 7 | OK | FAULT | FAULT

## CHILLER PUMPS
Main Page Title | Meter | Motor Run Status
Chiller Summary | PRY CHW PUMP 1 | OFF
| PRY CHW PUMP 2 | OFF
| PRY CHW PUMP 3 | OFF
| PRY CHW PUMP 4 | OFF
| CDS PUMP 1 | OFF
| CDS PUMP 2 | OFF
| CDS PUMP 3 | OFF
| CDS PUMP 4 | OFF
| TEST PRY | ON
| TEST CDS | OFF