## AHU
Main Page Title | Meter | Auto/Manual Status | Action | STATUS | COMMAND | Command vs Status Check | RAT | RAT Value Status | VFD Control | VFD Monitoring | Temperature Setpoint | CHW VALVE MODULATION | CHW Feedback | CHW Status | Delta | Recommended Valve Opening | Valve Opening Status Comment | COMMENT
AHU Summary North Side | AHU 1st Floor NS | AUTO | CHECK | OFF | OFF | OK | 23.1 | OK | 10 | -0.01 | 24 | 0 | 0 | OK | -0.9 | 0 | OK | NONE
| AHU 2nd Floor NS | AUTO | CHECK | OFF | OFF | OK | 28.9 | OK | 20 | -0.01 | 24 | 0 | 0 | OK | 4.9 | 100 | FAULT | Valve is not open as per the requirement
| AHU 3rd Floor NS | AUTO | CHECK | ON | ON | OK | 25.8 | OK | 45 | -0.01 | 24 | 45.2 | 45.2 | OK | 1.8 | 100 | FAULT | Valve is not open as per the requirement
| AHU 4th Floor NS | AUTO | CHECK | ON | ON | OK | 21.879 | OK | 60 | -0.04 | 20.09 | 0 | 44.37 | FAULT | 1.789 | 100 | FAULT | Valve is not open as per the requirement
| AHU 5th Floor NS | AUTO | CHECK | ON | ON | OK | 22.5 | OK | 47 | -0.01 | 18 | 100 | 100 | OK | 4.5 | 100 | OK | NONE
| AHU 6th Floor NS | AUTO | CHECK | ON | ON | OK | 20.9 | OK | 15 | -0.01 | 18 | 73.3 | 60 | FAULT | 2.9 | 100 | FAULT | Valve is not open as per the requirement
| AHU 7th Floor NS | AUTO | CHECK | ON | ON | OK | 20.5 | OK | 16 | -0.01 | 16 | 100 | 89 | FAULT | 4.5 | 100 | OK | NONE
| AHU 8th Floor NS | AUTO | CHECK | ON | ON | OK | 25.8 | OK | 14 | -0.01 | 20 | 100 | 97 | FAULT | 5.8 | 100 | OK | NONE
| AHU 9th Floor NS | AUTO | CHECK | ON | ON | OK | 23.17 | OK | 100 | -0.03 | 23.12 | 29.22 | 27.32 | FAULT | 0.05 | 0 | FAULT | Valve is open more than requirement
AHU Summary South Side | AHU 1st Floor SS | AUTO | CHECK | OFF | ON | FAULT | 30 | OK | 20 | -0.02 | 18 | 100 | 100 | OK | 12 | 100 | OK | NONE
| AHU 2nd Floor SS | MANUAL | XX | ON | OFF | XX | 35 | FAULT | 30 | -0.02 | 20 | 58 | 58 | OK | 15 | 100 | OK | NONE
| AHU 3rd Floor SS | MANUAL | XX | OFF | ON | XX | 16 | FAULT | 80 | -0.02 | 22 | 80 | 80 | OK | -6 | 0 | OK | NONE
| AHU 4th Floor SS | AUTO | CHECK | ON | ON | OK | 20.98 | OK | 60 | -0.02 | 22.72 | 80 | 59.03 | FAULT | -1.74 | 0 | FAULT | Valve is open more than requirement
| AHU 5th Floor SS | AUTO | CHECK | ON | ON | OK | 22.79 | OK | 98.5 | -0.03 | 24.94 | 0 | 0.45 | FAULT | -2.15 | 0 | OK | NONE
| AHU 6th Floor SS | AUTO | CHECK | ON | ON | OK | 22.89 | OK | 100 | -0.04 | 23.52 | 0 | 2.01 | FAULT | -0.63 | 0 | OK | NONE
| AHU 7th Floor SS | MANUAL | XX | ON | ON | XX | 20 | OK | 20 | -0.06 | 20 | 0 | 0 | OK | 0 | 0 | OK | NONE
| AHU 8th Floor SS | MANUAL | XX | OFF | ON | XX | 10 | FAULT | 46 | -0.06 | 20 | 0 | 0 | OK | -10 | 0 | OK | NONE
| AHU 9th Floor SS | AUTO | CHECK | OFF | ON | FAULT | 25 | OK | 32 | -0.06 | 20 | 100 | 100 | OK | 5 | 100 | OK | NONE

## Ambiant
Meter | Reading | Status
Ambiant Temperature | 40.8 | OK
Ambiant Relative Humidity(RH) | 35.06 | FAULT

## CHILLERS
Main Page Title | Meter | Chiller Status | Condenser Valve Status | Evaporator Valve Status | Condensor VALVE COMMENT | Evaporator VALVE COMMENT | Evaporator Inlet | Evaporator Outlet | Delta | Evaporator Inlet Status | Evaporator Outlet Status | Evaporator Delta Status
Chiller Summary | Chiller-1 | OFF | OFF | OFF | OK | OK | 10 | 4 | 6 | FAULT | FAULT | FAULT
| Chiller-2 | ON | OFF | OFF | FAULT | FAULT | 12 | 3 | 9 | OK | FAULT | FAULT
| Chiller-3 | OFF | OFF | OFF | OK | OK | 11 | 7 | 4 | FAULT | OK | OK
| Test Chiller-1 | ON | OFF | ON | FAULT | OK | 15 | 7 | 8 | FAULT | OK | FAULT
| Test Chiller-2 | ON | ON | OFF | OK | FAULT | 12 | 5 | 7 | OK | FAULT | FAULT

## CHILLER PUMPS
Main Page Title | Meter | Motor Run Status
Chiller Summary | PRY CHW PUMP 1 | OFF
| PRY CHW PUMP 2 | OFF
| PRY CHW PUMP 3 | OFF
| PRY CHW PUMP 4 | OFF
| CDS PUMP 1 | OFF
| CDS PUMP 2 | OFF
| CDS PUMP 3 | OFF
| CDS PUMP 4 | OFF
| TEST PRY | ON
| TEST CDS | OFF

## Chiller Integration
Meter | Compressor Status | Ampere | Run Hrs
Compressor 1 | ON | 165 | 143
Compressor 2 | ON | 145.5 | 984
| Chiller Flow | 0

## Energy Meters
Meter | kWH
EM1 | -28278.56
EM2 | -58299.46
EM3 | 52223.7

## Sheet1
Column1 | Column2 | Column3 | Column4 | Column5
Chiller And Pump
43251.5649 | SRE:DDC01'B'DDC01'AmbientRh.PrVal_B'DDC01'TAmbTemp | 40.8
43251.5649 | SRE:DDC01'B'DDC01'AmbientT.PrVal_B'DDC01'TAmbRh | 35.06
AHU
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'VFDMon.PrVal_B'DDC05'4LvlAHU'Trends'VFDMon | -0.04 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'AMSts.PrVal_B'DDC05'4LvlAHU'Trends'AM | 1 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'CHWMon.PrVal_B'DDC05'4LvlAHU'Trends'CHWMon1 | 44.37 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'CHWValve.PrVal_B'DDC05'4LvlAHU'Trends'CHWV | 0 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'RAT.PrVal_B'DDC05'4LvlAHU'Trends'RAT | 21.879 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'RTemp.PrVal_B'DDC05'4LvlAHU'Trends'RTemp | 20.09 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'RunSts.PrVal_B'DDC05'4LvlAHU'Trends'Run | 1 |  | T
43251.5503 | SRE:DDC05'B'DDC05'4LvlAHU'VFDCtrl.PrVal_B'DDC05'4LvlAHU'Trends'VFDCtrl | 60 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'AMSts.PrVal_B'DDC10'9LvlAHU'Trends'AM | 1 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'CHWMon.PrVal_B'DDC10'9LvlAHU'Trends'CHWMon1 | 27.32 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'CHWValve.PrVal_B'DDC10'9LvlAHU'Trends'CHWV | 29.22 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'RAT.PrVal_B'DDC10'9LvlAHU'Trends'RAT | 23.17 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'RTemp.PrVal_B'DDC10'9LvlAHU'Trends'RTemp | 23.12 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'RunSts.PrVal_B'DDC10'9LvlAHU'Trends'Run | 1 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'VFDCtrl.PrVal_B'DDC10'9LvlAHU'Trends'VFDCtrl | 100 |  | T
43251.5502 | SRE:DDC10'B'DDC10'9LvlAHU'VFDMon.PrVal_B'DDC10'9LvlAHU'Trends'VFDMon | -0.03 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'AMSts.PrVal_B'DDC14'4LvlAHU'Trends'AM | 1 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'CHWMon.PrVal_B'DDC14'4LvlAHU'Trends'CHWMon1 | 59.03 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'CHWValve.PrVal_B'DDC14'4LvlAHU'Trends'CHWV | 0 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'RAT.PrVal_B'DDC14'4LvlAHU'Trends'RAT | 20.98 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'RTemp.PrVal_B'DDC14'4LvlAHU'Trends'RTemp | 22.72 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'RunSts.PrVal_B'DDC14'4LvlAHU'Trends'Run | 1 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'VFDCtrl.PrVal_B'DDC14'4LvlAHU'Trends'VFDCtrl | 60 |  | T
43251.5503 | SRE:DDC14'B'DDC14'4LvlAHU'VFDMon.PrVal_B'DDC14'4LvlAHU'Trends'VFDMon | -0.02 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'AMSts.PrVal_B'DDC15'5LvlAHU'Trends'AM | 1 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'CHWMon.PrVal_B'DDC15'5LvlAHU'Trends'CHWMon1 | 0.45 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'CHWValve.PrVal_B'DDC15'5LvlAHU'Trends'CHWV | 0 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'RAT.PrVal_B'DDC15'5LvlAHU'Trends'RAT | 22.79 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'RTemp.PrVal_B'DDC15'5LvlAHU'Trends'RTemp | 24.94 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'RunSts.PrVal_B'DDC15'5LvlAHU'Trends'Run | 1 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'VFDCtrl.PrVal_B'DDC15'5LvlAHU'Trends'VFDCtrl | 98.5 |  | T
43251.5503 | SRE:DDC15'B'DDC15'5LvlAHU'VFDMon.PrVal_B'DDC15'5LvlAHU'Trends'VFDMon | -0.03 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'AMSts.PrVal_B'DDC16'6LvlAHU'Trends'AM | 1 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'CHWMon.PrVal_B'DDC16'6LvlAHU'Trends'CHWMon1 | 2.01 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'CHWValve.PrVal_B'DDC16'6LvlAHU'Trends'CHWV | 0 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'RAT.PrVal_B'DDC16'6LvlAHU'Trends'RAT | 22.89 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'RTemp.PrVal_B'DDC16'6LvlAHU'Trends'RTemp | 23.52 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'RunSts.PrVal_B'DDC16'6LvlAHU'Trends'Run | 1 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'VFDCtrl.PrVal_B'DDC16'6LvlAHU'Trends'VFDCtrl | 100 |  | T
43251.5505 | SRE:DDC16'B'DDC16'6LvlAHU'VFDMon.PrVal_B'DDC16'6LvlAHU'Trends'VFDMon | -0.04 |  | T
BTU Chiller & Energy Meters
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'BTU'ModSlvB'B1CUMFL.PrVal_B'DDC01'SoftIntg'BTU'ModSlvB'TB1CUMFL | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'BTU'ModSlvB'B1KWH.PrVal_B'DDC01'SoftIntg'BTU'ModSlvB'TB1KWH | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'BTU'ModSlvB'B1RETTEMP.PrVal_B'DDC01'SoftIntg'BTU'ModSlvB'TB1RTEMP | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'BTU'ModSlvB'B1SUPTEMP.PrVal_B'DDC01'SoftIntg'BTU'ModSlvB'TB1STEMP | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C1Amps.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC1Amps | 165 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C1Cap.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC1Cap | 88.8 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C1DisTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC1DisTem | 54.4 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C1LOL.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC1LOL | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C1RunHr.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC1RunHr | 143 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C1Sts.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC1Sts | 1 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C2Amps.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC2Amps | 145.5 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C2Cap.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC2Cap | 96.6 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C2DisTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC2DisTem | 50.9 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C2LOLT.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC2LOLT | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C2RunHr.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC2RunHr | 984 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'C2Sts.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TC2Sts | 1 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'ChCmd.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TChCmd | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'ChRunHr.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TChRunHr | 237 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'DisPres1.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TDisPres1 | 193 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'DisPres2.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TDisPres2 | 197 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'FLdAmps1.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TFLdAmps1 | 124 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'FLdAmps2.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TFLdAmps2 | 126 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'LoWFlow.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TLoWFlow | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'LWTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TLWTemp | 7.9 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'LWtempSP.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TLWtempSP | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'RWTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TRWTemp | 12.2 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'SPres1.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TSPres1 | 64 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'SPres2.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TSPres2 | 61 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'SysSts.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TSysSts | 3689 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch1'Target.PrVal_B'DDC01'SoftIntg'ChIntg'Ch1Trends'TTarget | 99.5 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C1Amps.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C1Amps | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C1Cap.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C1Cap | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C1DisTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C1DisTemp | 37.9 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C1LOL.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C1LOL | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C1RunHr.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C1RunHr | 261 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C1Sts.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C1Sts | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C2Amps.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C2Amps | 155.5 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C2Cap.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C2Cap | 97.7 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C2DisTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C2DisTemp | 55.9 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C2LOLT.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C2LOLT | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'C2Sts.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'C2Sts | 1 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'ChRunHr.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'ChRunHr | 617 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'DisPres1.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'DisPres1 | 13 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'DisPres2.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'DisPres2 | 260 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'FLdAmps1.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'FLdAmps1 | 119 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'FLdAmps2.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'FLdAmps2 | 160 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'LoWFlow.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'LoWFlow | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'LWTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'LWTemp | 8.2 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'LWtempSP.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'LWtempSP | 0 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'RWTemp.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'RWTemp | 12.7 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'SPres1.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'SPres1 | 14 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'SPres2.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'SPres2 | 69 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'SysSts.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'SysSts | 3823 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'ChIntg'Ch2'Target.PrVal_B'DDC01'SoftIntg'ChIntg'Ch2Trends'Target | 100 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'Curra.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1Curra | 34.24 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'Currb.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1Currb | 34.27 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'Currc.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1Currc | 35.61 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'Frq.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1Frq | 49.86 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'KWH.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1KWH | -28278.56 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'PF.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1PF | 0.74 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'TActp.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1TActp | -17917.73 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'TApp.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1TApp | 24324.09 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'TRep.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1TRep | -2635.6 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'VLtab.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1VLtab | 405.04 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'VLtbc.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1VLtbc | 405.71 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM1'VLtca.PrVal_B'DDC01'SoftIntg'EM'EM1'TEM1VLtca | 403.17 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'Curra.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2Curra | 21.93 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'Currb.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2Currb | 24.6 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'Currc.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2Currc | 26.26 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'Frq.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2Frq | 49.86 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'KWH.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2KWH | -58299.46 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'PF.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2PF | 0.59 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'TActp.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2TActp | -9958.51 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'TApp.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2TApp | 16978.56 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'TRep.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2TRep | 1584.03 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'VLtab.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2VLtab | 405.28 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'VLtbc.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2VLtbc | 405.85 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM2'VLtca.PrVal_B'DDC01'SoftIntg'EM'EM2'TEM2VLtca | 403.31 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'Curra.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3Curra | 0.22 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'Currb.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3Currb | 0.27 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'Currc.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3Currc | 0.23 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'Frq.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3Frq | 49.86 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'KWH.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3KWH | 52223.7 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'PF.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3PF | 0.24 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'TActp.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3TActp | 41.62 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'TApp.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3TApp | 174.83 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'TRep.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3TRep | -102.17 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'VLtab.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3VLtab | 406.55 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'VLtbc.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3VLtbc | 406.82 |  | T
43251.5649 | SRE:DDC01'B'DDC01'SoftIntg'EM'EM3'VLtca.PrVal_B'DDC01'SoftIntg'EM'EM3'TEM3VLtca | 404.89 |  | T
VFD
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'Ch1'Ch1EM.PrVal_B'VFDIntg'AHUVFD'Trends'TCh1EM | 1275956.12
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'Ch2'Ch2EM.PrVal_B'VFDIntg'AHUVFD'Trends'TCh2EM | 1254761.25
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'DC'DCEM.PrVal_B'VFDIntg'AHUVFD'Trends'TDCEM | 853868.19
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'LiftDB'LiftEM.PrVal_B'VFDIntg'AHUVFD'Trends'TLiftEM | 78072.95
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'MLDB'MLDBEM.PrVal_B'VFDIntg'AHUVFD'Trends'TMLDBEM | 775043
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'APow10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TAPow10 | 1.24
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'ASpd10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TASpd10 | 1211
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'AVC10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TAVC10 | 4.68
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'CntrPro10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TCntrPr10 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'DCV10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TDCV10 | 544
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'Eng10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TEng10 | 12356
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'FltSts10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TFltSts10 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'OFreq10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TOFreq10 | 40.37
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'OV10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TOV10 | 336
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'RunSts10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TRunSts10 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'Trq10.PrVal_B'VFDIntg'AHUVFD'NSAHU'1stVFDNS'TTrq10 | 9.9
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'APow11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TAPow11 | 1.39
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'ASpd11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TASpd11 | 1359
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'AVC11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TAVC11 | 4.64
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'CntrPro11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TCntrPr11 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'DCV11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TDCV11 | 542
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'Eng11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TEng11 | 9941
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'FltSts11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TFltSts11 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'OFreq11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TOFreq11 | 45.3
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'OV11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TOV11 | 376
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'RunSts11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TRunSts11 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'Trq11.PrVal_B'VFDIntg'AHUVFD'NSAHU'2ndVFDNS'TTrq11 | 9.85
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'APow12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TAPow12 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'ASpd12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TASpd12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'AVC12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TAVC12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'CntrPro12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TCntrPr12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'DCV12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TDCV12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'Eng12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TEng12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'FltSts12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TFltSts12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'OFreq12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TOFreq12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'OV12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TOV12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'RunSts12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TRunSts12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'Trq12.PrVal_B'VFDIntg'AHUVFD'NSAHU'3rdVFDNS'TTrq12 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'APow13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TAPow13 | 1.35
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'ASpd13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TASpd13 | 1453
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'AVC13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TAVC13 | 4.65
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'CntrPro13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TCntrPr13 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'DCV13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TDCV13 | 543
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'Eng13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TEng13 | 6462
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'FltSts13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TFltSts13 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'OFreq13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TOFreq13 | 48.45
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'OV13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TOV13 | 401
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'RunSts13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TRunSts13 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'Trq13.PrVal_B'VFDIntg'AHUVFD'NSAHU'4thVFDNS'TTrq13 | 8.96
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'APow14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TAPow14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'ASpd14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TASpd14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'AVC14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TAVC14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'CntrPro14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TCntrPr14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'DCV14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TDCV14 | 553
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'Eng14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TEng14 | 9283
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'FltSts14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TFltSts14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'OFreq14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TOFreq14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'OV14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TOV14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'RunSts14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TRunSts14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'Trq14.PrVal_B'VFDIntg'AHUVFD'NSAHU'5thVFDNS'TTrq14 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'APow15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TAPow15 | 2.53
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'ASpd15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TASpd15 | 1499
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'AVC15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TAVC15 | 4.34
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'CntrPro15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TCntrPr15 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'DCV15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TDCV15 | 539
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'Eng15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TEng15 | 9052
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'FltSts15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TFltSts15 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'OFreq15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TOFreq15 | 49.99
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'OV15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TOV15 | 402
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'RunSts15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TRunSts15 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'Trq15.PrVal_B'VFDIntg'AHUVFD'NSAHU'6thVFDNS'TTrq15 | 16.19
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'APow16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TAPow16 | 0.77
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'ASpd16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TASpd16 | 1098
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'AVC16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TAVC16 | 3.83
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'CntrPro16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TCntrPr16 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'DCV16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TDCV16 | 543
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'Eng16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TEng16 | 8149
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'FltSts16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TFltSts16 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'OFreq16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TOFreq16 | 36.6
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'OV16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TOV16 | 305
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'RunSts16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TRunSts16 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'Trq16.PrVal_B'VFDIntg'AHUVFD'NSAHU'7thVFDNS'TTrq16 | 6.75
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'APow17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TAPow17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'ASpd17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TASpd17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'AVC17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TAVC17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'CntrPro17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TCntrPr17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'DCV17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TDCV17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'Eng17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TEng17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'FltSts17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TFltSts17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'OFreq17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TOFreq17 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'OV17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TOV17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'RunSts17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TRunSts17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'Trq17.PrVal_B'VFDIntg'AHUVFD'NSAHU'8thVFDNS'TTrq17 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'APow18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TAPow18 | 3.28
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'ASpd18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TASpd18 | 1499
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'AVC18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TAVC18 | 7.08
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'CntrPro18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TCntrPr18 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'DCV18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TDCV18 | 539
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'Eng18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TEng18 | 13807
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'FltSts18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TFltSts18 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'OFreq18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TOFreq18 | 49.99
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'OV18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TOV18 | 402
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'RunSts18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TRunSts18 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'Trq18.PrVal_B'VFDIntg'AHUVFD'NSAHU'9thVFDNS'TTrq18 | 21.05
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'PDB01'PDB01EM.PrVal_B'VFDIntg'AHUVFD'Trends'TPDB01EM | 653040.5
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'PDB02'PDB02EM.PrVal_B'VFDIntg'AHUVFD'Trends'TPDB02EM | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'PDB03'PDB03EM.PrVal_B'VFDIntg'AHUVFD'Trends'TPDB03EM | 59806.99
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'APow19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TAPow19 | 16.7
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'ASpd19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TASpd19 | 2935
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'AVC19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TAVC19 | 27.32
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'CntrPro19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TCntrPr19 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'DCV19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TDCV19 | 541
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'Eng19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TEng19 | 25596
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'FltSts19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TFltSts19 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'OFreq19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TOFreq19 | 48.92
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'OV19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TOV19 | 401
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'RunSts19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TRunSts19 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP1VFD'Trq19.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP1VFD'TTrq19 | 54.43
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'APow20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TAPow20 | 9.58
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'ASpd20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TASpd20 | 2636
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'AVC20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TAVC20 | 18.12
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'CntrPro20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TCntrPr20 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'DCV20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TDCV20 | 554
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'Eng20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TEng20 | 44223
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'FltSts20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TFltSts20 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'OFreq20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TOFreq20 | 43.94
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'OV20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TOV20 | 342
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'RunSts20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TRunSts20 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP2VFD'Trq20.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP2VFD'TTrq20 | 34.89
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'APow21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TAPow21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'ASpd21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TASpd21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'AVC21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TAVC21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'CntrPro21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TCntrPr21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'DCV21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TDCV21 | 562
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'Eng21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TEng21 | 50728
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'FltSts21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TFltSts21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'OFreq21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TOFreq21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'OV21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TOV21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'RunSts21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TRunSts21 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'PPVFD'PP3VFD'Trq21.PrVal_B'VFDIntg'AHUVFD'PPVFD'PP3VFD'TTrq21 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'APow1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TAPow1 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'ASpd1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TASpd1 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'AVC1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TAVC1 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'CntrPr1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TCntrPr1 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'DCV1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TDCV1 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'Eng1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TEng1 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'FltSts1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TFltSts1 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'OFreq1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TOFreq1 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'OV1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TOV1 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'RunSts1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TRunSts1 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'Trq1.PrVal_B'VFDIntg'AHUVFD'SSAHU'1stVFDSS'TTrq1 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'APow2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TAPow2 | 1.43
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'ASpd2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TASpd2 | 1356
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'AVC2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TAVC2 | 4.41
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'CntrPr2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TCntrPr2 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'DCV2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TDCV2 | 539
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'Eng2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TEng2 | 7494
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'FltSts2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TFltSts2 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'OFreq2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TOFreq2 | 45.22
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'OV2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TOV2 | 375
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'RunSts2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TRunSts2 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'Trq2.PrVal_B'VFDIntg'AHUVFD'SSAHU'2ndVFDSS'TTrq2 | 10.16
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'APow3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TAPow3 | 1.71
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'ASpd3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TASpd3 | 1357
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'AVC3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TAVC3 | 4.59
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'CntrPr3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TCntrPr3 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'DCV3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TDCV3 | 542
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'Eng3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TEng3 | 9178
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'FltSts3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TFltSts3 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'OFreq3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TOFreq3 | 45.24
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'OV3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TOV3 | 362
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'RunSts3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TRunSts3 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'Trq3.PrVal_B'VFDIntg'AHUVFD'SSAHU'3rdVFDSS'TTrq3 | 12.14
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'APow4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TAPow4 | 0.64
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'ASpd4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TASpd4 | 901
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'AVC4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TAVC4 | 3.96
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'CntrPr4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TCntrPr4 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'DCV4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TDCV4 | 545
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'Eng4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TEng4 | 9317
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'FltSts4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TFltSts4 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'OFreq4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TOFreq4 | 30.05
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'OV4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TOV4 | 251
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'RunSts4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TRunSts4 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'Trq4.PrVal_B'VFDIntg'AHUVFD'SSAHU'4thVFDSS'TTrq4 | 6.84
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'APow5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TAPow5 | 2.16
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'ASpd5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TASpd5 | 1483
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'AVC5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TAVC5 | 5.3
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'CntrPr5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TCntrPr5 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'DCV5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TDCV5 | 540
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'Eng5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TEng5 | 8366
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'FltSts5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TFltSts5 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'OFreq5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TOFreq5 | 49.45
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'OV5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TOV5 | 395
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'RunSts5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TRunSts5 | 1
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'Trq5.PrVal_B'VFDIntg'AHUVFD'SSAHU'5thVFDSS'TTrq5 | 14
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'APow6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TAPow6 | 1.76
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'ASpd6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TASpd6 | 1499
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'AVC6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TAVC6 | 4.87
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'CntrPr6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TCntrPr6 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'DCV6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TDCV6 | 541
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'Eng6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TEng6 | 7724
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'FltSts6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TFltSts6 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'OFreq6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TOFreq6 | 49.99
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'OV6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TOV6 | 403
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'RunSts6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TRunSts6 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'Trq6.PrVal_B'VFDIntg'AHUVFD'SSAHU'6thVFDSS'TTrq6 | 11.31
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'APow7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TAPow7 | 0.53
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'ASpd7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TASpd7 | 905
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'AVC7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TAVC7 | 3.6
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'CntrPr7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TCntrPr7 | 0
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'DCV7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TDCV7 | 545
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'Eng7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TEng7 | 9312
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'FltSts7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TFltSts7 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'OFreq7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TOFreq7 | 30.19
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'OV7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TOV7 | 243
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'RunSts7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TRunSts7 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'Trq7.PrVal_B'VFDIntg'AHUVFD'SSAHU'7thVFDSS'TTrq7 | 5.69
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'APow8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TAPow8 | 1.05
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'ASpd8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TASpd8 | 1204
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'AVC8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TAVC8 | 4.14
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'CntrPr8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TCntrPr8 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'DCV8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TDCV8 | 539
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'Eng8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TEng8 | 8424
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'FltSts8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TFltSts8 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'OFreq8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TOFreq8 | 40.15
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'OV8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TOV8 | 334
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'RunSts8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TRunSts8 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'Trq8.PrVal_B'VFDIntg'AHUVFD'SSAHU'8thVFDSS'TTrq8 | 8.43
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'APow9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TAPow9 | 3.36
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'ASpd9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TASpd9 | 1499
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'AVC9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TAVC9 | 7.4
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'CntrPr9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TCntrPr9 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'DCV9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TDCV9 | 539
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'Eng9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TEng9 | 16411
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'FltSts9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TFltSts9 | 0
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'OFreq9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TOFreq9 | 49.99
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'OV9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TOV9 | 402
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'RunSts9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TRunSts9 | 1
43251.5939 | SRE:DDC21'B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'Trq9.PrVal_B'VFDIntg'AHUVFD'SSAHU'9thVFDSS'TTrq9 | 21.57
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'TRFO01'TRFO01EM.PrVal_B'VFDIntg'AHUVFD'Trends'TTRFO01EM | 2813661.5
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'TRFO02'TRFO02EM.PrVal_B'VFDIntg'AHUVFD'Trends'TTRFO02EM | 2939763.75
43251.594 | SRE:DDC21'B'VFDIntg'AHUVFD'VentDB'VentEM.PrVal_B'VFDIntg'AHUVFD'Trends'TVentEM | 44616.21