## AHU
Main Page Title | Meter | Auto/Manual Status | Action | STATUS | COMMAND | Command vs Status Check | RAT | RAT Value Status | VFD Control | Temperature Setpoint | CO Sensor | CO Setpoint (PPM) | CO Sensor Status | Fresh Air Damper Control | Reccomended Damper Oppening | Damper Opening Status | CHW VALVE MODULATION | Delta | Recommended Valve Opening | Valve Opening Status Comment | COMMENT
AHU Summary | AHU 1st Floor | AUTO | CHECK | OFF | OFF | OK | 27.45 | OK | 70 | 23 | 317.8 | 500 | OK | 50 | 0 | FAULT | 100 | 4.45 | 100 | OK | NONE
| AHU 2nd Floor | AUTO | CHECK | OFF | OFF | OK | 25.77 | OK | 70 | 23 | 538.4 | 500 | OK | 0 | 25.12 | FAULT | 0 | 2.77 | 100 | FAULT | Valve is not open as per the requirement
| AHU 3rd Floor | AUTO | CHECK | OFF | OFF | OK | 25.28 | OK | 80 | 23 | 642.66 | 500 | OK | 0 | 39.0213 | FAULT | 0 | 2.28 | 100 | FAULT | Valve is not open as per the requirement
| AHU 5th Floor | AUTO | CHECK | OFF | OFF | OK | 27.13 | OK | 70 | 23 | 380.6 | 500 | OK | 0 | 20 | FAULT | 0 | 4.13 | 100 | FAULT | Valve is not open as per the requirement
| AHU 6th Floor | AUTO | CHECK | OFF | OFF | OK | 27.4 | OK | 80 | 23 | 575.4 | 500 | OK | 0 | 30.0533 | FAULT | 0 | 4.4 | 100 | FAULT | Valve is not open as per the requirement
| AHU GRND Floor | AUTO | CHECK | OFF | OFF | OK | 29.13 | OK | 0 | 23 | 423.8 | 500 | OK | 50 | 20 | FAULT | 0 | 6.13 | 100 | FAULT | Valve is not open as per the requirement

## Fans
Meter | Status
BATTERY ROOM SENSOR ALARM | OFF
EX FAN 1 RUN STATUS | OFF
EX FAN 2 RUN STATUS | ON
EX FAN 3 RUN STATUS | ON
EX FAN 4 RUN STATUS | OFF
EX FAN 5 RUN STATUS | OFF
EX FAN 6 RUN STATUS | OFF
EX FAN 7 RUN STATUS | OFF
EX FAN 8 RUN STATUS | OFF
EX FAN 9 RUN STATUS HIGH | OFF
EX FAN 9 RUN STATUS LOW | OFF
EX FAN 10 RUN STATUS HIGH | OFF
EX FAN 10 RUN STATUS LOW | OFF
FRESH AIR FAN 2 RUN STATUS | ON
FRESH AIR FAN 1 RUN STATUS | OFF
JET FAN FAN 1 RUN STATUS HIGH | OFF
JET FAN FAN 1 RUN STATUS LOW | OFF
JET FAN FAN 2 RUN STATUS HIGH | OFF
JET FAN FAN 2 RUN STATUS LOW | OFF
JET FAN FAN 3 RUN STATUS HIGH | OFF
JET FAN FAN 3 RUN STATUS LOW | OFF
JET FAN FAN 4 RUN STATUS HIGH | OFF
JET FAN FAN 4 RUN STATUS LOW | OFF
JET FAN FAN 5 RUN STATUS HIGH | OFF
JET FAN FAN 5 RUN STATUS LOW | OFF
JET FAN FAN 6 RUN STATUS HIGH | OFF
JET FAN FAN 6 RUN STATUS LOW | OFF

## Cooling Towers
Meter | Status | Valve Command IN | Valve Command OUT | Valve FB IN | Valve FB OUT | Water Entering Temperature (Celcius) | Water Leaving Temperature (Celcius)
CT 1 LOW LEVEL | OFF | ON | ON | OFF | ON | 42.37 | 31.49
CT2 LOW LEVEL | OFF | ON | ON | ON | OFF | 42.24 | 31.54
CT3 LOW LEVEL | OFF | ON | ON | ON | ON | 43.45 | 33.2

## UPS
Meter | Alarm Flag | BAT Volt (V) | BAT Current (A) | Bypass Frequency (Hz) | INPUT VOLT A B (V) | INPUT VOLT B C (V) | INPUT VOLT C A (V) | Output Active Power A (kW) | Output Active Power B (kW) | Output Active Power C (kW) | Output Current A (A) | Output Current B (A) | Output Current C (A) | Output Volt A (V) | Output Volt B (V) | Output Volt C (V)
UPS 1 | LOW | 462.9 | 1 | 49.92 | 404.8 | 403.3 | 403.7 | 27 | 42 | 15 | 6.5 | 9.6 | 4.1 | 230 | 229.3 | 229.7
UPS 2 | LOW | 463.2 | 1 | 49.92 | 406.7 | 403.7 | 404.1 | 27 | 41 | 15 | 8.2 | 10.7 | 4.2 | 229.1 | 228.8 | 229.7

## VFD
Meters | Actual Active Power (Kw) | Actual Torque Value (N/m) | Actual Current (A) | Control Priorith | DC Link Voltage (V) | Energy Consumption (Kwh) | Fault Status | Run Status | Speed Actual Value
VFD 1 SEC P 1 | 0 | 0 | 0 | 0 | 575 | 3457 | 0 | OFF | 0
VFD 2 SEC P 2 | 0 | 0 | 0 | 0 | 579 | 3599 | 0 | OFF | 0
VFD 3 SEC P 3 | 0 | 0 | 0 | 0 | 0 | 3243 | 0 | OFF | 0
VFD 4 HRW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OFF | 0

## CHILLERS
Main Page Title | Meter | Chiller Run Status | Chiller Start/Stop Status | Run vs Status Check
Chiller Summary | ATC 1 | OFF | OFF | OK
| ATC 2 | OFF | OFF | OK
| ATC 3 | OFF | OFF | OK

## Terrace Fan
Meter | Run Status | Start Stop Status
PRES FAN 1 | OFF | OFF
PRES FAN 2 | OFF | OFF

## Chiller Integration
Meter | Alarm Status | Current Unit Load | Entering Water Temp. | Flow Switch Status | Leaving Water Temp | Run Status | Temperature Setpoint
Chiller 1 | LOW | 0 | 32.6 | OFF | 33.2 | OFF | 7
Chiller 2 | LOW | 3 | 32.9 | OFF | 34 | OFF | 7
Chiller 3 | LOW | 1 | 33.3 | OFF | 34 | OFF | 7

## PAC
Meter | RUN Status | RETURN Rh SETPOINT (%) | Return Rh Value (%) | Return Temp Setpoint | Return Temp
PAC 1 | ON | 50 | 74.2 | 23 | 23.9
PAC2 | OFF | 50 | 74.2 | 23 | 25.6

## Energy Meter
Meter | Active Power (kW) | Forward Active Energy (Kwh)
EM1 | 4e-18 | 1892.6351
EM2 | 202.9397 | 4693.2773
EM3 | 4e-18 | 6083.3892
EM4 | 4e-18 | 6762.6982
EM5 | 4e-18 | 5867.1289
EM6 | 924.9614 | 5740.9678
EM7 | 81.105 | 0
EM8 | 243.1517 | 0
EM9 | 0 | 8905.7344
EM10 | 4e-18 | 8905.7344
EM11 | 4e-18 | 8905.7344
EM12 | 5174.2988 | 724.1033
EM13 | 5779.1841 | 2490.4553
EM14 | 1844.8186 | 2.9729e-17
EM15 | 3626.605 | 2490.4553
EM16 | 0 | 0
EM17 | 0 | 2.9729e-17
EM18 | 1198.7454 | 67203.0391
EM19 | 474.3329 | 49590.2148
EM20 | 176.1181 | 43068.9062
EM21 | 510.1747 | 49397.8828
EM22 | 1465.7926 | 33189.1133
EM23 | 2352.8171 | 0
EM24 | 0 | 0
EM25 | 1615.9495 | 8910.0059
EM26 | 4e-18 | 3737.6895
EM27 | 720.4658 | 2706.9272
EM28 | 4e-18 | 6454.8945

## HRW
Meter | Run Status | Start/Stop Status | Return Fan Start Stop | Return Fan Run Status | Return Temperature | Supply Fan Speed Control (%) | Supply Fan Run Status | Supply Fan Start Stop | Supply Temperature
HR 1 | OFF | OFF | OFF | OFF | 45.16 | 50 | OFF | OFF | 30.63